[image: image5.emf]How to Connect Wonderware InSQL to the TOP Server


This paper is not intended to provide the reader with knowledge on how to use InSQL in general.  It is assumed the reader knows how to use InSQL and knows what data they want to store.  This paper was created using Version 9.0 of InSQL but should work with other versions of InSQL, older or newer, that use the same methodology of connecting to I/O Servers.  No specific version of TOP Server is required, though it’s always a good idea to have the latest version since upgrades are freely available at http://www.toolboxopc.com/wonderware. 

Step 1) Configure the TOP Server: 

[image: image6.png]|3 Console window il

Tree | Favories |

Conscle Ract
gy IndustrialSQL Server
5 B IncustiaSaL Server Group
5 B CWaksIR 04
&l Monagement Consdle





In this example we will be using the TOP Server simulation driver configuration.  For more information on how to setup TOP Server, see the Training Videos or Papers and Utilities links at the website below: http://www.toolboxopc.com/wonderware/
You will need at least one Channel and one Device in the TOP Server in order to log data in InSQL.  Tags can be entered into the TOP Server if desired, but these can also be added in the item field in InSQL to avoid duplicate tag database entries.  This is the approach this paper follows and is shown later in this paper.

Step2) Configure New I/O Server Type in InSQL

[image: image7.png]Track Modfications,
ot Perding Changes:
Import Tags,

New Window fram Here:
' Refresh

Help



[image: image8.png]Console Root
ey, Industrial5Q Server
=) B IndustrilsL Server Group
58 veeWakIR-SP
1] Mansgement Conscle
& 5] Confouration Edtor
(=1 System Configuration
&1 Parameters
=2 Data Acqustion
o
£ System river
£} 10AS- YPCWKSHR5P4
22 MDis{Manual Tags




Open InSQL and go to the Configuration Editor in the console tree.  Open the tree then go to the 

[image: image9.emf]
I/O Server Types.  Right click on the I/O Server Types to show the drop down menu.  Select New I/O Server Type as shown below.

The New I/O Server window will open and should be filled out as the properties window below shows.  

[image: image10.png]Console Root
ey, Industrial5Q Server
2 8 ndustriatsL. Server Group
58 veeWakIR-SP
1] Mansgement Conscle
& 5] Confouration Edtor
(=1 System Configuration
&1 Parameters
=2 Data Acqstion
3 1/0 Server Types
£ systemoriver
583 IDAS - VPC-WRKSHR:SPS

3 MDAS Menul Togs
Storage





It is key that the Application name is ServerMain and the Exe Name is servermain.exe.  You can set the Platform type as needed for your application.  

Once the New I/O Server Type is added you can add the TOP Server as an I/O Server to your InSQL Node.

Step3) Configure New I/O Server in InSQL

[image: image11.png]. Track Modfications,
Commit Pending Changss.
Import Tags,

New Window from Here:
New Taskpad View.

au
Delete
Refresh
Export List,

Properties

Help




In this example the Node is selected under Data Acquisition.  When you right click, choose New I/O Server as shown.

[image: image12.png]Console Root
ey, Industrial5Q Server
2 8 ndustriatsL. Server Group
58 veeWakIR-SP
1] Mansgement Conscle
& 5] Confouration Edtor
(=1 System Configuration
&1 Parameters
=2 Data Acqstion
3 1/0 Server Types
£ system river





When the New I/O Server Window opens you will be able to enter the I/O Server Location where the TOP Server is installed.  Use localhost as the I/O Server Location if InSQL and the TOP Server are on the same PC.  

[image: image13.png]Track Madfications.
ot Perding Changes:
Import Tags,

New Window fram Here:
Refresh
Properties

Help



If you set the New I/O Server Type correctly as above, you will be able to select ServerMain from the drop down list under I/O Server Type.  Below you will see the Protocol Type set as SuiteLink.  If the TOP Server is not on the same PC as InSQL you must make sure that the Wonderware or Factory Suite Common Components are installed on the PC where TOP Server is located for SuiteLink to work. These components can be found on your Wonderware installation CDs.  Contact your local Wonderware support if you need help installing the Factory Suite Common Components.

Once this is complete you can click Finish.  

Step4) Configure New Topic in InSQL

Now highlight the new I/O server you just created in the Console Tree as shown below.  Right Click and choose New Topic from the list.

[image: image14.png]1/0 Server Locatia:

10 Server Type:

Protacel Type

& SuiteLink

Desciption

Al Server Locatia:

locahost

© DDE

Covel |t





[image: image15.png]TOP Server - [Ci\Program i

Fie | Edt View Users Tools He
D¢ Und cilfz
E

New Chanel

New Device,
fiew Tan Group
ey Tag,

au i

g o ctee
paste gy

g Delete Dl

Properties.




[image: image1.png]10 Server

Topic Name:

Time Out;

WacahostServerMain

[Channel_

I~ 5etToNoTime Out

50000

Device_1

Ceel |t





The New Topic window is shown above.  The Topic Name entered needs to be in the format of the Channel name followed by the Device Name you have in the TOP Server, separated with an underscore (_).  This can be seen in the TOP Server Alias Map. New Aliases or Topics can be added in the TOP Server Alias Map.  In the TOP Server, we use the name Alias instead of Topic. 

[image: image16.png]o @ = = ST

Alos MappedTo Seani=,
D Chemnel_0_User_Defined_Sine Chennel0_User Defined S 0
D) Chemnel_0_Uset Defined_Sine_Syst. Chanel 0_User_Defined Sine_System 0
D) Chamnel_0_User Defined_User Chennel0_User Delined User 0
D) Chemnel_0_Uset_Defined_Usr_Syst.. Channel 0. User_Defned User_System 0
) Chamnel 1 System Chemel_1_System o
. :
D) Chamel_1_Device_1_System Chemnel_1 Device_1_System 0
) Channe1 Device_ Chemel_1 Device_2 0
D Chemel_1 Device_2_sysem Chemnel_1 Device_2_System o =
) Chamnel_2_System Chemel 2_System 0
) Chamne_2 Device_3 Chemnel_2Device_3 0
D Chemel_2 Device_3_system Chemnel_2Device_3_System 0
) Chamnel_3_System Chemel_3_System 0
) Channe 3 Device_4 Chemnel 3 Device_4 0
@) Charnel_3_Device_4_System Charnel_3Device_4,_System | 0 _'_I
‘

Close. Help




You get to the Alias Map in the TOP Server by going to the TOP Server menu and choosing Edit then selecting Alias Map.

When the Alias Map opens you will see the Window below.  The Alias column shows the list of Alias names or Topics.  If you uncheck the box “Show aliases for system generated groups,” only Aliases you create will be shown.  To create new Aliases you can click on the shield and star icon , the left most icon shown on the Alias Map dialog.

[image: image17.png]Mappedto: [Channel 1 Device_1

Sean ate averide: =] millseconds

E-47 Channe0_User_Defined 7
_System
& ] Ram
System
& Rardom
_System
& [ sme
_System
& U
_system
=147 Channel 1
_System

= Device_1
S





Double Click on an Alias to show details.

[image: image18.png]Console Root
ey, Industrial5Q Server
=) B IndustrilsL Server Group
58 veeWakIR-SP
1] Mansgement Conscle
& 5] Confouration Edtor
(=1 System Configuration
&1 Parameters
=2 Data Acqstion
3 1/0 Server Types
£ systemoriver
583 DS - VPCWRKSHR:SP4
21 59 WocshstToPServer





The Name field shows the Topic or Alias name to use in InSQL.  The Scan rate override is the rate you want the TOP Server to Poll the items in that topic.  The default setting of zero shown will result in 100 millisecond scan rates for all items in the topic.  By setting the Scan Rate Override here, you can control tag scan or poll rate for all items in the topic, so you don’t need to set the scan rate on individual tags if you have created these in the TOP Server.

After you verify your Topic name and set yoru Scan rate override for the Topic in the TOP Server, make any other changes to the New Topic dialog in InSQL and click Finish.  The Time Out setting is for the connection to TOP Server from InSQL and does not affect TOP Server to device timeouts. Consult your InSQL documentation on advice on the Time Out setting. 

[image: image2.png]10 Server

Topic Name:

Time Out;

WacahostServerMain

[Channel_

I~ 5etToNoTime Out

50000

Device_1

Ceel |t





Once the new topic is created you can now click Finish and start adding tags.  

Step5) Configure New Tag in InSQL

[image: image19.png]Track Wedfications,

Commit Pending Changss.
Import Tags,

New Dicrete Tag,
New Event Tag.
New string Tag.
Fier

View
New Window from Here:

New Taskpad View.

Dekete
Refresh
Export List,

Properties

Help





This example will show a simple addition of an Analog tag.

[image: image20.png][New Analog Tag

Urique Tag Nare:





Right click on the Topic then choose the tag type that you want to create.

The Unique Tag Name is the name you want shown in InSQL and can be any meaningful name.  In this example we have used testtag1. 

[image: image21.png]Description: =

Min,Vale: nEU)

100

Ma. Value:
Curent Edtor —————————————————
& InsaL © InTouch





The General Window is for setting Engineering Units inside of InSQL

[image: image22.png]Console Root
gy IndustrialSQL Server
5 B IncustiaSaL Server Group
5 B CWaksIR 04
&l Monagement Consdle

System Confgurstion
&1 Parameters
=2 Data Acqstion
3 1/0 Server Types
£ systemoriver
583 DS - VPCWRKSHR:SP4

21 59 WecshostToPServer

{24 Topi: Channel_i_Device_t





Click on the Next button once you have this filled out as needed.  The example shown does not set any scaling or Engineering Units.

In the Acquisition dialog the critical first piece is the Item name.  The Acquisition Type, I/O Server and Topic Name should all default to what you have configured.  If they don’t appear correctly, then select them from the drop down lists.

The Item Name field can be the PLC address for the data you want to read through TOP Server into InSQL, or a tag name in the TOP Server that you have configured.  If the PLC address if being used then refer to the Addressing section in the TOP Server driver help file for the particular driver you are using to verify that the default data type is the same as the data type you want returned as set in the Raw Type setting.  In this example we want a 16 bit unsigned integer.  

[image: image3.png][New Analog Tag testtag! - Acqui

Acquistion Typs: |70 Server Acauisiton =
10 Server \acahost T0PServer |
Channel_1_Device_1 =l

[Roo0

Topic Name:

Item Name:

- RawType.

©ineger € Real Integer e TV -

Seaing

© Linear & None i Fa | iz, e 1120
oo [Too | _caed | e |





In the TOP Server simulation driver, the address R0001 defaults to a 16 bit signed Integer data type.  This will require the Item name to have an “@datatype” suffix added to the name to tell TOP Server to send back the data in the datatype to match the setting in the Raw Type area in InSQL.  

[image: image23.png]New Analog Tag testtagl - Storage

|- Storage Method Active Image.
® Dalerz) & Active Image contains al eceived valies
& Cycle
€ Deta € Active Image contains ol stored values
- Storage Stetegy

Rate:  [5Seconds ¥ Samples InActive Inage:
Tine Deadaer |” ms) Vel Deadber (%EU)

o | G|t





For example; R0001@WORD will return a 16 bit unsigned integer.  In a Modbus driver you may want to read holding register 400001 as a real.  This would require the Item Name to be 400001@FLOAT.  If you wanted to read this as an unsigned integer you would use simply 400001 in the item name because the Modbus driver by default treats all “4” registers as 16 bit unsigned integers or Words.

Once the Acquisition dialog is complete, fill out the Storage dialog as needed and click the Finish button.

Step6) Commit Pending Changes in InSQL

It’s now time to commit the configuration changes in InSQL.  Highlight the Configuration Editor and right click then select Commit Pending Changes.

[image: image24.png]Track Modifications,

Import Tags.

View »
New Window from Here:

New Taskpad View.
Refresh

Help




[image: image25.png]m Computer Neme: VPCW2KSVRSP4

Do you want to conit pending changes now?

Select Display' o view pending changes, o Commit to 3pply
changes now.

T | = | E





Once Commit Pending Changes is selected the Confirmation dialog below will open.  If this dialog does not open you will need to right click on Configuration Editor in the Console tree again and select Commit Pending Changes.  If you are not able to see this dialog Confirmation, contact your Wonderware Distributor for InSQL Support.

[image: image26.png]Console Root
gy IndustrialSQL Server
5 B IncustiaSaL Server Group
5 B CwaksR 04
155 management Console

Dta Acquistion

16 clents

History Blocks
D Log

51 Confguration o
= ystem Corfiguration




Once the Confirmation dialog appears choose Commit to commit the changes or Display to check the changes make then Commit them after you have verified them.

This finishes the configuration process and it’s now time to start collecting data.

Step7) Start Data Collection in InSQL

Highlight the Status item in the Console tree and right click on it.  Choose “Start InSQL”.

[image: image27.png]Stop In50L
Al Tasks »

View »
New Window from Here:

New Taskpad View.

Refresh

Help




[image: image28.png]Console Root
gy IndustrialSQL Server
5 B IncustiaSaL Server Group
5 B CwaksR 04
155 management Console

160 Cients

3 Fistory Hocks




The dialog below should pop-up.

[image: image4.png][Start InSQL Server

Gensl |

@ Start InSEL Server

Fress DK to Stat InSQL Server on the following InS0L
Server

Server [VPEwaKavR Pe

Cance

Help





Click on the OK button, once this is done you can watch all the data collection engines starting in the Status Window.  When the data collection items go to green you can then highlight the Data Acquisition in the Console Tree as shown below.

[image: image29.png]Computer Topic Protocol | Tags | Status | values

©rcvasi s ircuasn s s swank o Rectvng 2273





If the connection has been made correctly you will see the item as highlighted below.[image: image30.png]]

(Cients: 0 [Active tags: D oF 0





If the item with ServerMain does not turn green, completely stop InSQL and start it again.  If you continue to have problems go to Step 8 to check the TOP Server.

Step8) Verify Connection in TOP Server

The first thing to check is if a connection has been made from InSQL to TOP Server and the number of active tags in TOP Server.  This should be done first with the OPC Quick Client shut down.  Verifying the connection is done by looking and the bottom right of the TOP Server as shown below.

[image: image31.png](Clents: 1 [Active tags: 1 of 1





[image: image32.png]Date Time. User Name_| Source. Event
€ 101212005 10:25:55AM  Default User  TOP Server  Opering project C:\Program Fils|Software
€ 101212005 10:25:55AM  Default User  TOP Server  Simulator device iver loaded successfuly.
€ 101212005 10:25:55AM  Default User  TOP Server  Starting Simulator device drver.

@ 10/21/2005 1025555 AM  Default User  Simulator  Simulator Device Driver ¥4.31,91 - U
@11/9/2005  2:5550PM  Default User  TOP Server  Toolbox OPC Power Server Started
@11/5/2005  2558:57PM  Default User  TOP Server  Opering project C:\Program Fils|Software
€ 11/5/2005 _ 2:58:57 P Default User  TOP Server _ Simulstor device iver loaded successfully.

@ 11j92005

2857 PH

Default User

Simator

Simlator Device Driver Y4.31.91 - U




The image on the left above shows the server without a connection, the image on the right above shows the connection completed from Step 4.  The number of Active tags should match the number of tags that are configured in the InSQL project.  This is a good way to verify all your tags are connected.  If there is any difference or there is no connection made check the TOP Server Event Log as shown below.

[image: image33.png]-0}
3

vgre




The Event Log shown in this example has no errors.  If there is a syntax error in the Topic or the Item field in the InSQL configuration errors will be shown in this log.  These need to be resolved in order to get consistent quality data from all tags.  If the error was in the syntax of the Topic or the item field has an invalid address for the device type the error will say, “Failed to add FastDDE/SuiteLink item…”  This could prevent the connection from being made if there are not correct items.  This will need to be resolved before you will be able to get the green icon in the Data Acquisitions section from Step7.  

If there are no errors in the TOP Server Event Log and no connection to the server is made, the problem is either in the InSQL configuration or with the installation of the Wonderware common components.  First verify all the steps in this document.  

If the configuration seems correct, then you may want to consider a reinstallation of InSQL if that is feasible.  You may also want to involve your local Wonderware distributor support staff and ask them to contact us and work with us on any TOP Server questions.  We can work with your local Wonderware support team to help get things working.  

Also, once you have reached this point please contact us at support@softwaretoolbox.com for additional help in checking your configuration.  Please send the following files in a zip file along with any other information that would help us to understand your configuration and application requirements. 

- Servermain.log - found at \Program Files\Software Toolbox\TOP Server

- Servermain.ini - also found at \Program Files\Software Toolbox\TOP Server

- Your TOP Server project *.opf file

�








�





�





�





�











( Copyright Software Toolbox Inc. 2002-2005, All Rights Reserved Worldwide.  All trademarks are property of their respective owners.

- 1 -

